Environmental Monitoring Guaranteed Data Delivery Methods

In this existence where chaos runs rampant, and entropy furthers us into an eventual heat death. Environmental Monitoring needs to be there to not lose any recordings due to connectivity loss to the server. That is where guaranteed data delivery, henceforth known as GDD, becomes important to store temperature measurements and eventually send them back to the server once connection is restored.

900MHz Only (For G3 and below):

Starting chronologically on when theses schemes were first designed and implemented, the first method is 900 MHz Only.

The GDD method first begins when the tag does not receive an acknowledgement from the star. The tag will retry the same packet 3 more times in rapid succession regardless of report rate. If even after this there is no acknowledgement from the star, the tag will begin storing temperature measurement data into its memory buffer.  One thing to note is that even if the temperature measured is outside of its alert range. GDD measurements will always be ones taken at the slower report rate and not the measurement rate (Local alerts will still activate if a measured temperature is out of range during a measurement rate reading).

While still disconnected with the server the tag will continue to record the report rate temperature measurements until 8,640 measurements have been stored. At 5 minute report rate this comes out to be 30 days.  Once this limit has been reached, the oldest data point is overwritten with the current data point. Because of its cyclical nature there is an index value inside the EM tag that points to keep track of the oldest data point throughout.

Once the temperature tag successfully pages into the system, it will need to send all the stored temperature measurements to the server.  The tag will send old temperature readings over 900MHz every 3 seconds on a FIFO basis. This data will be transmitted on the location frequency. If the report cycle for temperature data measurement comes up while the tag is sending stored data, the current temperature data will be added to the end of the list.  If the tag is set to both probes, the 900MHz offline measurement packet contains both Probe 1 and Probe 2 data.

Upload stored data process is as follows:

- The tag will send a page request to the

- The star will send an ack to the tag

- Tag will transmit 1 stored data point

- Star will send an ack for each pack

- Tag will delete the sent data from memory

- If any data remains stored in tag memory, tag will send another request to upload data 3 seconds later

On G3 and below tags there is no Real Time Clock, RTC, so the EM tag does not actually know what time a measurement is taken. The timestamp of each measurement is instead handled by the server.  If it’s a current measurement the server will just slap the current time and call it a day. For GDD data, the server receives an extra variable called Offline Measurement Count along with the Raw data from the EM tag.  The Offline Measurement Count starts at 0 and increments by 1 every time the tag restores a new temperature measurement. The count then caps at 8,640 as the maximum number of data points gets reached.

Using the count, the server can calculate the measured timestamp using the following equation:

Offline Temperature Timestamp= (Current  Time) - (Offline Measurement Count * Report Rate)

If the Report Rate setting is ever changed in the profile, the GDD buffer is cleared of all data even if it has not reported to the server. This is to prevent wrong timestamps from being assigned to data points as the server has no way of knowing if a data point came from the new or old report rate.

The GDD is also cleared when a manual reset is performed on the tag as it cannot distinguish a manual reset or a reset caused by a dead battery. This is to once again ensure we have correct timestamps associated with each data point.

It has been stated before the packet transfers happen once every 3 seconds between the tag and the server. This causes the Current Time value mentioned above to drift. To compensate for this drift every 20 reports (60 seconds), the server subtracts an additional minute from the Offline Temperature Timestamp regardless of report rate. This means while looking at a log for a tag that has done/doing GDD there will be a time jump every 20 reports, but is not a bug in the server.

CCX (Cisco) GDD (All EM Tags):

CCX GDD is easier to understand than 900MHz Only as GDD will constantly be cycling through the same 8,640 data points and transmitting them through Cisco packets regardless connection to the system. The CCX packet will always have the same 37 data points. This means if the tag takes a measurement at 8:00 AM on January 30th 2022, the CCX GDD packet being sent to the server will contain the following:

| Data Point | Time since measurement | Example |
| --- | --- | --- |
| 1 | Current Measurement | 1/30/2022 8:00 |
| 2 | 1 hour before | 1/30/2022 7:00 |
| 3 | 2 hours | 1/30/2022 6:00 |
| 4 | 3 hours | 1/30/2022 5:00 |
| 5 | 4 hours | 1/30/2022 4:00 |
| 6 | 5 hours | 1/30/2022 3:00 |
| 7 | 6 hours | 1/30/2022 2:00 |
| 8 | 1 day before | 1/29/2022 8:00 |
| 9 | 2 days | 1/28/2022 8:00 |
| 10 | 3 days | 1/27/2022 8:00 |
| 11 | 4 days | 1/26/2022 8:00 |
| 12 | 5 days | 1/25/2022 8:00 |
| 13 | 6 days | 1/24/2022 8:00 |
| 14 | 7 days | 1/23/2022 8:00 |
| 15 | 8 days | 1/22/2022 8:00 |
| 16 | 9 days | 1/21/2022 8:00 |
| 17 | 10 days | 1/20/2022 8:00 |
| 18 | 11 days | 1/19/2022 8:00 |
| 19 | 12 days | 1/18/2022 8:00 |
| 20 | 13 days | 1/17/2022 8:00 |
| 21 | 14 days | 1/16/2022 8:00 |
| 22 | 15 days | 1/15/2022 8:00 |
| 23 | 16 days | 1/14/2022 8:00 |
| 24 | 17 days | 1/13/2022 8:00 |
| 25 | 18 days | 1/12/2022 8:00 |
| 26 | 19 days | 1/11/2022 8:00 |
| 27 | 20 days | 1/10/2022 8:00 |
| 28 | 21 days | 1/9/2022 8:00 |
| 29 | 22 days | 1/8/2022 8:00 |
| 30 | 23 days | 1/7/2022 8:00 |
| 31 | 24 days | 1/6/2022 8:00 |
| 32 | 25 days | 1/5/2022 8:00 |
| 33 | 26 days | 1/4/2022 8:00 |
| 34 | 27 days | 1/3/2022 8:00 |
| 35 | 28 days | 1/2/2022 8:00 |
| 36 | 29 days | 1/1/2022 8:00 |
| 37 | 30 days | 12/31/2021 8:00 |

Then during the next report at 8:05 AM, all the data points will be in respect to the new time of 8:05 AM instead of 8:00AM, giving new data. With this design, CCX GDD under good coverage will never take more than a day to recover the GDD.

One downside of the above method is that the EM tag does not know which data points are missing like in 900MHz only nor can the server request certain data points from the buffer. This can then result where a certain data point will be missing for a long time because after 6 hours have passed from the original measurement, the tag will send this data point in a CCX packet only once a day. If this time slot has heavy traffic, it could take several days for GDD to fill completely. This outside CenTrak Engineering’s control and is more of a case-by-case basis with the hospital.

Once again as in 900MHz GDD, the tag sends an Offline Measurement Count along with each Raw Temp value, though not it is no longer incremented and instead associated with whatever place in the temperature measurement buffer it is in from 0 to 8,640. The way Offline Timestamp is calculated is also the same so whenever the Report Rate setting is changed or the tag is manually reset GDD will wipe.

ACX (Aruba) GDD ( All EM Tags):

Aruba works the exact same as Cisco GDD, except the Aruba packets are smaller so we had to spread out the data points. Each Aruba GDD packet contains 6 two hour interval data points along with 15 two day interval data points. If we once again use our 8:00 AM on January 30th 2022 example along with the next day 8:00 AM on January 31th 2022 to get the full 30 days:

| Data Point | Time since measurement | Example | Example 2 |
| --- | --- | --- | --- |
| 1 | Current Measurement | 1/30/2022 8:00 | 1/31/2022 8:00 |
| 2 | 2 hours before | 1/30/2022 6:00 | 1/31/2022 6:00 |
| 3 | 4 hours | 1/30/2022 4:00 | 1/31/2022 4:00 |
| 4 | 6 hours | 1/30/2022 2:00 | 1/31/2022 2:00 |
| 5 | 8 hours | 1/30/2022 0:00 | 1/31/2022 0:00 |
| 6 | 10 hours | 1/30/2022 22:00 | 1/31/2022 22:00 |
| 7 | 12 hours | 1/30/2022 20:00 | 1/31/2022 20:00 |
| 9 | 2 days | 1/28/2022 8:00 | 1/29/2022 8:00 |
| 11 | 4 days | 1/26/2022 8:00 | 1/27/2022 8:00 |
| 13 | 6 days | 1/24/2022 8:00 | 1/25/2022 8:00 |
| 15 | 8 days | 1/22/2022 8:00 | 1/23/2022 8:00 |
| 17 | 10 days | 1/20/2022 8:00 | 1/21/2022 8:00 |
| 19 | 12 days | 1/18/2022 8:00 | 1/19/2022 8:00 |
| 21 | 14 days | 1/16/2022 8:00 | 1/17/2022 8:00 |
| 23 | 16 days | 1/14/2022 8:00 | 1/15/2022 8:00 |
| 25 | 18 days | 1/12/2022 8:00 | 1/13/2022 8:00 |
| 27 | 20 days | 1/10/2022 8:00 | 1/11/2022 8:00 |
| 29 | 22 days | 1/8/2022 8:00 | 1/9/2022 8:00 |
| 31 | 24 days | 1/6/2022 8:00 | 1/7/2022 8:00 |
| 33 | 26 days | 1/4/2022 8:00 | 1/5/2022 8:00 |
| 35 | 28 days | 1/2/2022 8:00 | 1/3/2022 8:00 |
| 37 | 30 days | 12/31/2021 8:00 | 1/1/2022 8:00 |

This means GDD will take two full days to fully repopulate the 30 days. Once again connectivity to the Aruba AP could cause delays and missed aruba packets will take two more days to send that data point again.

As stated in previous sections, if report rate is changed or a manual reset is performed, GDD will be wiped.

UDP/TCP GDD (G3 and Onwards):

UDP/TCP GDD structures its GDD packets in the same way CCX does with 37 data points: Current Measurement, 6 past hours on that minute, and the last 30 days at this currently measured time. The difference is that a UDP/TCP tag will transmit a packet that contains of 3 GDD packets  every 15 minutes in order to save power.  This behavior is shown below:

At 30 minute report rate, the tag will send 2 of the above packets every 30 minutes. At 60 minute report rate, the tag will send 4 packets every 60 minutes. Finally, GDD still gets wiped with Report Rate changes or when the tag is manually reset.